## Arkusz1
Address | Size | Name | Type | Units | Description
40190 | 1 | M_AC_Current | int16 | Amps | AC Current (sum of active phases)
40191 | 1 | M_AC_Current_A | int16 | Amps | Phase A AC Current
40192 | 1 | M_AC_Current_B | int16 | Amps | Phase B AC Current
40193 | 1 | M_AC_Current_C | int16 | Amps | Phase C AC Current
40194 | 1 | M_AC_Current_S F | int16 | SF | AC Current Scale Factor
40195 | 1 | M_AC_Voltage_L N | int16 | Volts | Line to Neutral AC Voltage (average of active phases)
40196 | 1 | M_AC_Voltage_A N | int16 | Volts | Phase A to Neutral AC Voltage
40197 | 1 | M_AC_Voltage_B N | int16 | Volts | Phase B to Neutral AC Voltage
40198 | 1 | M_AC_Voltage_C N | int16 | Volts | Phase C to Neutral AC Voltage
40199 | 1 | M_AC_Voltage_L L | int16 | Volts | Line to Line AC Voltage (average of active phases)
40200 | 1 | M_AC_Voltage_A B | int16 | Volts | Phase A to Phase B AC Voltage
40201 | 1 | M_AC_Voltage_B C | int16 | Volts | Phase B to Phase C AC Voltage
40202 | 1 | M_AC_Voltage_C A | int16 | Volts | Phase C to Phase A AC Voltage
40203 | 1 | M_AC_Voltage_S F | int16 | SF | AC Voltage Scale Factor
40204 | 1 | M_AC_Freq | int16 | Herts | AC Frequency
40205 | 1 | M_AC_Freq_SF | int16 | SF | AC Frequency Scale Factor
40206 | 1 | M_AC_Power | int16 | Watts | Total Real Power (sum of active phases)
40207 | 1 | M_AC_Power_A | int16 | Watts | Phase A AC Real Power
40208 | 1 | M_AC_Power_B | int16 | Watts | Phase B AC Real Power
40209 | 1 | M_AC_Power_C | int16 | Watts | Phase C AC Real Power
40210 | 1 | M_AC_Power_SF | int16 | SF | AC Real Power Scale Factor
40211 | 1 | M_AC_VA | int16 | Volt- Amps | Total AC Apparent Power (sum of active phases)
40212 | 1 | M_AC_VA_A | int16 | Volt- Amps | Phase A AC Apparent Power
40213 | 1 | M_AC_VA_B | int16 | Volt- Amps | Phase B AC Apparent Power
40214 | 1 | M_AC_VA_C | int16 | Volt- Amps | Phase C AC Apparent Power
40215 | 1 | M_AC_VA_SF | int16 | SF | AC Apparent Power Scale Factor
40216 | 1 | M_AC_VAR | int16 | VAR | Total AC Reactive Power (sum of active phases)
40217 | 1 | M_AC_VAR_A | int16 | VAR | Phase A AC Reactive Power
40218 | 1 | M_AC_VAR_B | int16 | VAR | Phase B AC Reactive Power
40219 | 1 | M_AC_VAR_C | int16 | VAR | Phase C AC Reactive Power
40220 | 1 | M_AC_VAR_SF | int16 | SF | AC Reactive Power Scale Factor
40221 | 1 | M_AC_PF | int16 | % | Average Power Factor (average of active phases)
40222 | 1 | M_AC_PF_A | int16 | % | Phase A Power Factor
40223 | 1 | M_AC_PF_B | int16 | % | Phase B Power Factor
40224 | 1 | M_AC_PF_C | int16 | % | Phase C Power Factor
40225 | 1 | M_AC_PF_SF | int16 | SF | AC Power Factor Scale Factor
40226 | 2 | M_Exported | uint32 | Watt- hours | Total Exported Real Energy
40228 | 2 | M_Exported_A | uint32 | Watt- hours | Phase A Exported Real Energy
40230 | 2 | M_Exported_B | uint32 | Watt- hours | Phase B Exported Real Energy
40232 | 2 | M_Exported_C | uint32 | Watt- hours | Phase C Exported Real Energy
40234 | 2 | M_Imported | uint32 | Watt- hours | Total Imported Real Energy
40236 | 2 | M_Imported_A | uint32 | Watt- hours | Phase A Imported Real Energy
40238 | 2 | M_Imported_B | uint32 | Watt- hours | Phase B Imported Real Energy
40240 | 2 | M_Imported_C | uint32 | Watt- hours | Phase C Imported Real Energy
40242 | 1 | M_Energy_W_SF | int16 | SF | Real Energy Scale Factor
40243 | 2 | M_Exported_VA | uint32 | VA-hours | Total Exported Apparent Energy
40245 | 2 | M_Exported_VA_ A | uint32 | VA-hours | Phase A Exported Apparent Energy
40247 | 2 | M_Exported_VA_ B | uint32 | VA-hours | Phase B Exported Apparent Energy
40249 | 2 | M_Exported_VA_ C | uint32 | VA-hours | Phase C Exported Apparent Energy
40251 | 2 | M_Imported_VA | uint32 | VA-hours | Total Imported Apparent Energy
40253 | 2 | M_Imported_VA_ A | uint32 | VA-hours | Phase A Imported Apparent Energy
40255 | 2 | M_Imported_VA_ B | uint32 | VA-hours | Phase B Imported Apparent Energy
40257 | 2 | M_Imported_VA_ C | uint32 | VA-hours | Phase C Imported Apparent Energy
40259 | 1 | M_Energy_VA_S F | int16 | SF | Apparent Energy Scale Factor
40260 | 2 | M_Import_VARh_ Q1 | uint32 | VAR-hours | Quadrant 1: Total Imported Reactive Energy
40262 | 2 | M_Import_VARh_ Q1A | uint32 | VAR-hours | Phase A - Quadrant 1: Imported Reactive Energy
40264 | 2 | M_Import_VARh_ Q1B | uint32 | VAR-hours | Phase B- Quadrant 1: Imported Reactive Energy
40266 | 2 | M_Import_VARh_ Q1C | uint32 | VAR-hours | Phase C- Quadrant 1: Imported Reactive Energy
40268 | 2 | M_Import_VARh_ Q2 | uint32 | VAR-hours | Quadrant 2: Total Imported Reactive Energy
40270 | 2 | M_Import_VARh_ Q2A | uint32 | VAR-hours | Phase A - Quadrant 2: Imported Reactive Energy
40272 | 2 | M_Import_VARh_ Q2B | uint32 | VAR-hours | Phase B- Quadrant 2: Imported Reactive Energy
40274 | 2 | M_Import_VARh_ Q2C | uint32 | VAR-hours | Phase C- Quadrant 2: Imported Reactive Energy
40276 | 2 | M_Export_VARh_ Q3 | uint32 | VAR-hours | Quadrant 3: Total Exported Reactive Energy
40278 | 2 | M_Export_VARh_ Q3A | uint32 | VAR-hours | Phase A - Quadrant 3: Exported Reactive Energy
40280 | 2 | M_Export_VARh_ Q3B | uint32 | VAR-hours | Phase B- Quadrant 3: Exported Reactive Energy
40282 | 2 | M_Export_VARh_ Q3C | uint32 | VAR-hours | Phase C- Quadrant 3: Exported Reactive Energy
40284 | 2 | M_Export_VARh_ Q4 | uint32 | VAR-hours | Quadrant 4: Total Exported Reactive Energy
40286 | 2 | M_Export_VARh_ Q4A | uint32 | VAR-hours | Phase A - Quadrant 4: Exported Reactive Energy
40288 | 2 | M_Export_VARh_ Q4B | uint32 | VAR-hours | Phase B- Quadrant 4: Exported Reactive Energy
40290 | 2 | M_Export_VARh_ Q4C | uint32 | VAR-hours | Phase C- Quadrant 4: Exported Reactive Energy
40292 | 1 | M_Energy_VAR_ SF | int16 | SF | Reactive Energy Scale Factor
40293 | 2 | M_Events | uint32 | Flags | See M_EVENT_ flags. 0 = nts.